## Revision Record Sheet
Revision | Modification
1.01 | Added information regardin the CPUM and count of the BF/AF
1.02 | Not release
1.03 | "XMV Config" sheet, remove DC Gap, this value was used wit the CMS, but has no meaning with VibroSight

## IP adresses
| CPUM | IP settings |  |  | Configuration
#1 | IP Adresse |  |  | OR | (1)
IP mask
Gateway
#2 | IP adresse
IP mask
Gateway
| XMV | Slot: | 10
XMV | IP Adresse #1 | (2)
IP mask
Gateway
XIO16T | IP adresse #2 | (2) |  | Disable
IP mask
Gateway
| XMV | Slot | 12
XMV | IP Adresse #1 | (2)
IP mask
Gateway
XIO16T | IP adresse #2 | (2) |  | Disable
IP mask
Gateway
Notes:
Please complete the colored cells
(1) | CPUM Standard configuration = 610-100-000:
IP#1 IP address: 10.10.56.56
IP#1 IP Netmask: 256.256.256.128
IP#1 Gateway: Not defined
IP#2 IP address: 10.10.56.156
IP#2 IP Netmask: 256.256.256.128
IP#2 Gateway: Not defined
Modbus configuration standard as described in Appendix A and B of the "VM600 networking manual MAVM600-NET/E Edition 8 - May 2015"
For any non-standard configuration a part number shall be delivered by Meggitt SA.
(2) | Can be set to DHCP, in that case IP mask and Gateway shall be left blank

## MPC Config.
MPC CONFIGURATION SLOTx ---- EXAMPLE ------
Channel | Input TAG No. | Front-end | Sensor OK Level | I/P SENS. | Transfer function | Processing | Filter settings | Rectifier | FSD | 4-20mA or 10,0V DC | Alarm Level | Danger Level | TM | DC O/P | Output TAG No.
CH. 1 | - TBD - | TQ 4X2/IQS450 | -1,6 ÷ -17,6 Volt | 4mV/µm |  | Relative Shaft | 205Hz | True peak to peak | 500µm | x | 200 / 0s / NonLatch | 300 / 3s / Latch | 2 | 1 | - TBD -
CH. 2 | - TBD - | TQ 4X2/IQS450[i] | -15500 ÷ -20500 µA | 1.25µA/µm |  | Relative Shaft | 205Hz | True peak to peak | 500µm | x |  |  |  | 2 | - TBD -
CH. 1 & 2
CH. 3 | - TBD - | CA202/IPC/GSI | 7000 ÷ 17000 µA | 77µA/mm/s | 7553.7 µA/pCs | BBAB | 10..1000Hz | RMS | 20 mm/s | x | 4 / 0s / NonLatch | 6 / 0s / NonLatch | 1 | 3 | - TBD -
CH. 4 | - TBD - | TQ 9X2/IQS900 | -1,6 ÷ -17,6 Volt | 4mV/µm |  | Relative Shaft | 205Hz | True peak to peak | 250µmpp | x |  |  |  | 4 | - TBD -
CH. 3 & 4
TACHO 1 | - TBD - | TQ 4X2/IQS450 |  | 4mV/µm |  | RPM or Hz |  |  | 1000 RPM | x |  |  |  |  | - TBD -
TACHO 2 | Not used
MPC CONFIGURATION SLOT 3
Channel | Input TAG No. | Front-end | Sensor OK Level | I/P SENS. | Transfer function | Processing | Filter settings | Rectifier | FSD | 4-20mA or 10,0V DC | Alarm Level | Danger Level | TM | DC O/P | Output TAG No.
CH. 1 | - TBD - | TQ 9X2/IQS900 | -1,6 ÷ -17,6 Volt | 4mV/µm |  | PS |  | DC | +/-1mm | x | +/-0.5mm | +/-1mm |  | 1 | - TBD -
CH. 2
CH. 1 & 2
CH. 3 | - TBD - | TQ912/IQS900 | -1,6 ÷ -17,6 Volt | 4mV/µm |  | Relative Shaft | 155 Hz | True peak to peak | 500µm
CH. 4 | - TBD - | TQ912/IQS900 | -1,6 ÷ -17,6 Volt | 4mV/µm |  | Relative Shaft | 155 Hz | True peak to peak | 500µm
CH. 3 & 4 | [5 empty] | DMF MAX 1&2 |  | True peak to peak | 500µm | x |  |  |  | 3 | - TBD -
TACHO 1
TACHO 2
MPC CONFIGURATION SLOT 4
Channel | Input TAG No. | Front-end | Sensor OK Level | I/P SENS. | Transfer function | Processing | Filter settings | Rectifier | FSD | 4-20mA or 10,0V DC | Alarm Level | Danger Level | TM | DC O/P | Output TAG No.
CH. 1 | - TBD - | TQ902/IQS900 | -1,6 ÷ -17,6 Volt | 4mV/µm |  | PS | -15701mV |  | 4 mm | [5 empty] | - TBD -
CH. 2 | - TBD - | TQ902/IQS900 | -1,6 ÷ -17,6 Volt | 4mV/µm |  | PS | -9600mV |  | 4 mm
CH. 1 & 2 | [5 empty] | RST 5° |  |  | -5…+40 mm | x |  |  |  | 1 | - TBD -
CH. 3 | - TBD - | TQ403/IQS900 | -1,6 ÷ -17,6 Volt | 1,33mV/µm |  | PS | -11918mV |  | 12 mm
CH. 4 | - TBD - | TQ902/IQS900 | -1,6 ÷ -17,6 Volt | 4mV/µm |  | PS | -9600mV |  | 4 mm
CH. 3 & 4 | [5 empty] | RST 5° |  |  | -5..+45 mm | x |  |  |  | 3 | - TBD -
TACHO 1
TACHO 2

## AMC Config.
AMC8 CONFIGURATION SLOT X ---- EXAMPLE ------ |  |  |  |  | Average |  | Alarms |  |  |  | DC O/P
Channel | Input TAG No. | I/P Type | I/P FSD | I/P Unit | Type | Period | D - | A - | A + | D + | No | FSD | Output TAG No.
CH. 1 | - TBD - | RTD (100 Ohm. PLATINE) | 0 à 120 | ˚C |  |  |  |  | 70 | 80 | 1 | 120 | - TBD -
CH. 2 | - TBD - | RTD (100 Ohm. PLATINE) | 0 à 120 | ˚C |  |  |  |  | 75 | 90 | 2 | 120 | - TBD -
CH. 3 | - TBD - | RTD (100 Ohm. PLATINE) | 0 à 120 | ˚C |  |  |  |  | 75 | 90 | 3 | 120 | - TBD -
CH. 4 | - TBD - | RTD (100 Ohm. PLATINE) | 0 à 120 | ˚C
CH. 5 | - TBD - | RTD (100 Ohm. PLATINE) | 0 à 120 | ˚C |  |  |  |  | 65 | 80 | 4 | 120 | - TBD -
CH. 6 | - TBD - | RTD (100 Ohm. PLATINE) | 0 à 120 | ˚C |  |  |  |  | 65 | 80 | 5 | 120 | - TBD -
CH. 7 | - TBD - | RTD (100 Ohm. PLATINE) | 0 à 120 | ˚C
CH. 8 | Not used
AMC8 CONFIGURATION SLOT 12 |  |  |  |  | Average |  | Alarms |  |  |  | DC O/P
Channel | Input TAG No. | I/P Type | I/P FSD | I/P Unit | Type | Period | D - | A - | A + | D + | No | FSD | Output TAG No.
CH. 1
CH. 2
CH. 3
CH. 4
CH. 5
CH. 6
CH. 7
CH. 8

## CMC Config (hidden)
CMC CONFIGURATION SLOT X SAMPLE SAMPLE SAMPLE SAMPLE
Channel | Input TAG No. | Signal Type | Front-end | Signal Origin | Linked Through | I/P SENS. | DC Offset | Current / Voltage |  | Fix. Freq. / Order Track. |  | Speed Ref. | Bandwidth | FSD
CH. 1 | Tacho1 | Speed | TQ401/IQS451 | MPC Slot Y Tacho Z | Tacho Bus |  | 0 | X | [5 empty] | 5000RPM
CH. 2 | Abs. Vib. 1 | Dynamic | CA 201/IPC 704 | MPC Slot Y Channel Z | Raw Bus | 77µA/mm/s | 0 | X |  | X |  |  | 10kHz | 20mm/s RMS
CH. 3 | Abs. Vib. 2 | Dynamic | CA 201/IPC 704 | MPC Slot Y Channel Z | Raw Bus | 77µA/mm/s | 0 | X |  | X |  |  | 10kHz | 20mm/s RMS
CH. 4 | Abs. Vib. 3 | Dynamic | CA 201/IPC 704 | MPC Slot Y Channel Z | Raw Bus | 77µA/mm/s | 0 | X |  | X |  |  | 10kHz | 20mm/s RMS
CH. 5 | Abs. Vib. 4 | Dynamic | CA 201/IPC 704 | MPC Slot Y Channel Z | Raw Bus | 77µA/mm/s | 0 | X |  | X |  |  | 10kHz | 20mm/s RMS
CH. 6 | Abs. Vib. 5 | Dynamic | CA 201/IPC 704 | MPC Slot Y Channel Z | Raw Bus | 77µA/mm/s | 0 | X |  | X |  |  | 10kHz | 20mm/s RMS
CH. 7 | Abs. Vib. 6 | Dynamic | CA 201/IPC 704 | MPC Slot Y Channel Z | Raw Bus | 77µA/mm/s | 0 | X |  | X |  |  | 10kHz | 20mm/s RMS
CH. 8 | Abs. Vib. 7 | Dynamic | CA 201/IPC 704 | MPC Slot Y Channel Z | Raw Bus | 77µA/mm/s | 0 | X |  | X |  |  | 10kHz | 20mm/s RMS
CH. 9 | Rel. Vib 1 X | Dynamic | TQ401/IQS451 | MPC Slot Y Channel Z | Raw Bus | 8mv/µm | 0 |  | X |  | X | Channel 1 | 25 Orders | 500µm
CH. 10 | Rel. Vib 1 Y | Dynamic | TQ401/IQS451 | MPC Slot Y Channel Z | Raw Bus | 8mv/µm | 0 |  | X |  | X | Channel 1 | 25 Orders | 500µm
CH. 11 | Rel. Vib 2 X | Dynamic | TQ401/IQS451 | MPC Slot Y Channel Z | Raw Bus | 8mv/µm | 0 |  | X |  | X | Channel 1 | 25 Orders | 500µm
CH. 12 | Rel. Vib 2 Y | Dynamic | TQ401/IQS451 | MPC Slot Y Channel Z | Raw Bus | 8mv/µm | 0 |  | X |  | X | Channel 1 | 25 Orders | 500µm
CH. 13 | Rel. Vib 3 X | Dynamic | TQ401/IQS451 | MPC Slot Y Channel Z | Raw Bus | 8mv/µm | 0 |  | X |  | X | Channel 1 | 25 Orders | 500µm
CH. 14 | Rel. Vib 3 Y | Dynamic | TQ401/IQS451 | MPC Slot Y Channel Z | Raw Bus | 8mv/µm | 0 |  | X |  | X | Channel 1 | 25 Orders | 500µm
CH. 15 | Rotation | Digital | RotXXX | External | Hard-Wired |  | 0 |  | X
CH. 16 | Temperature | Analog | TempXXX | AMC Slot Y Channel Z | Hard-Wired | 10mV/°C | 0 |  | X |  |  |  |  | 100°C

## XMV Config
XMV CONFIGURATION SLOT X ---- EXAMPLE ------
Channel | Input TAG No. | Signal Type | Front-end | Signal Origin | Linked Through | I/P SENS. | Current / Voltage |  | Fix. Freq. / Order Track. |  | Speed Ref. | Bandwidth | FSD
T1 | MAD13CY045 | Speed | Front-end | MPC Slot 3 Tacho 1 | Tacho Bus1 | 4 mv/µm |  | x |  |  |  |  | 5000RPM
T2 | MBA10CY101E | Speed | Front-end | MPC Slot 3 Tacho 2 | Tacho Bus2 | 4 mv/µm |  | x |  |  |  |  | 5000RPM
T3
T4
CH. 1 | MAD11CY041 | Dynamic | TQ4X2 / IQS450 | MPC Slot 3 Channel 1 | Raw Bus (0/32) | 4 mv/µm |  | x |  | X | T1 | 25 Orders | 500µm pp
CH. 2 | MAD11CY042 | Dynamic | TQ4X2 / IQS450 | MPC Slot 3 Channel 2 | Raw Bus (1/33) | 4 mv/µm |  | x |  | X | T1 | 25 Orders | 500µm pp
CH. 3
CH. 4
CH. 5 | MAD12CY041 | Dynamic | TQ4X2 / IQS450 | MPC Slot 4 Channel 1 | Raw Bus (4/36) | 4 mv/µm |  | x |  | X | T1 | 25 Orders | 500µm pp
CH. 6 | MAD12CY042 | Dynamic | TQ4X2 / IQS450 | MPC Slot 4 Channel 2 | Raw Bus (5/37) | 4 mv/µm |  | x |  | X | T1 | 25 Orders | 500µm pp
CH. 7 | MAD11CY021 | Dynamic | CA202/IPC 704 | MPC Slot 4 Channel 3 | Raw Bus (6/38) | 77µA/mm/s (24.9865mV/mm/s) |  | x |  | X | T1 | 25 Orders | 20 mm/ sec
CH. 8 | MAD12CY021 | Dynamic | CA202/IPC 704 | MPC Slot 4 Channel 4 | Raw Bus (7/39) | 77µA/mm/s (24.9865mV/mm/s) |  | x |  | X | T1 | 25 Orders | 20 mm/ sec
CH. 9 | MAD13CY041 | Dynamic | TQ4X2 / IQS450 | MPC Slot 5 Channel 1 | Raw Bus (8/40) | 4 mv/µm |  | x |  | X | T1 | 25 Orders | 500µm pp
CH. 10 | MAD13CY042 | Dynamic | TQ4X2 / IQS450 | MPC Slot 5 Channel 2 | Raw Bus (9/41) | 4 mv/µm |  | x |  | X | T1 | 25 Orders | 500µm pp
CH. 11 | MAD13CY021 | Dynamic | CA202/IPC 704 | MPC Slot 6 Channel 3 | Raw Bus (10/42) | 77µA/mm/s (24.9865mV/mm/s) |  | x |  | x | T1 | 25 Orders | 20 mm/ sec
CH. 12 | MAD13CY024 | Dynamic | CA202/IPC 704 | MPC Slot 6 Channel 4 | Raw Bus (11/43) | 77µA/mm/s (24.9865mV/mm/s) |  | x |  | x | T1 | 25 Orders | 20 mm/ sec
CH. 13 | MAD13CY043 | Dynamic | TQ4X2 / IQS450 | MPC Slot 6 Channel 1 | Raw Bus (12/44) | 4 mv/µm |  | x |  | X | T1 | 25 Orders | 500µm pp
CH. 14 | MAD13CY044 | Dynamic | TQ4X2 / IQS450 | MPC Slot 6 Channel 2 | Raw Bus (13/45) | 4 mv/µm |  | x |  | X | T1 | 25 Orders | 500µm pp
CH. 15 | MAD13CY045 | Dynamic | TQ 4X2/IQS450 | MPC Slot 7 Channel 3 | Hard wired* | 4mV/µm |  | x |  | X | T1 | 25 Orders | 500µmpp
CH. 16 | MBA10CY101E | Dynamic | TQ 4X2/IQS450 | MPC Slot 7 Channel 4 | Hard wired* | 4mV/µm |  | x |  | X | T1 | 25 Orders | 500µmpp
* SIL channel need to be "hard wired"
XMV CONFIGURATION SLOT 9
Channel | Input TAG No. | Signal Type | Front-end | Signal Origin | Linked Through | I/P SENS. | Current / Voltage |  | Fix. Freq. / Order Track. |  | Speed Ref. | Bandwidth | FSD
T1
T2
T3
T4
CH. 1
CH. 2
CH. 3
CH. 4
CH. 5
CH. 6
CH. 7
CH. 8
CH. 9
CH. 10
CH. 11
CH. 12
CH. 13
CH. 14
CH. 15
CH. 16
* SIL channel need to be "hard wired"

## IOC relays
[6 empty] | Number of BFs | [5 empty] | Number of AFs
[5 empty] | Slot: | 3 | 5 | - | - | - | - | 3 | 5 | - | - | - | -
Relay configuration IOC SLOT X (IOC4T) |  |  |  | ---- EXAMPLE ------
REL. No. | Output TAG No. | NE/NDE | NC/NO | SIGNALs LOCATION
RL1 | System OK | NE | NC | MPC running AND Common OK failure
RL2 | Danger_Ch1 | NE | NC | Danger Ch1
RL3 | Alarm_Ch2 | NE | NC | Alarm Ch2
RL4 | Danger_Ch2 | NE | NC | Danger CH2
Relay configuration IOC SLOT X (IOC8T) |  |  |  | ---- EXAMPLE ------
REL. No. | Output TAG No. | NE/NDE |  | SIGNALs LOCATION
RL1 | MBD11 CY101-XM71 | NE |  | OK CH. 1 AND MPC RUNNING
RL2 | MBD12 CY101-XM71 | NE |  | OK CH. 2 AND MPC RUNNING
RL3 | MKD10 CY101-XM71 | NE |  | OK CH. 3 AND MPC RUNNING
RL4 | MKD20 CY101-XM71 | NE |  | OK CH. 4 AND MPC RUNNING
RL5 | MKD21 CY101-XM71 | NE |  | OK CH. 5 AND MPC RUNNING
RL6 | MKD22 CY101-XM71 | NE |  | OK CH. 6 AND MPC RUNNING
RL7 | MKD30 CY101-XM71 | NE |  | OK CH. 7 AND MPC RUNNING
RL8 | MKD31 CY101-XM71 | NE |  | OK CH. 8 AND MPC RUNNING
[6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## RLC relays
Relay configuration RLC SLOT X SAMPLE SAMPLE SAMPLE SAMPLE |  |  | ---- EXAMPLE ------
REL. No. | Output TAG No. | NE/NDE | SIGNALs LOCATION
RL1 | MBM11 CP102C-XG01 | NE | MPC 4 SLOT 6 ALERT+ CH. 1
RL2 | MBM11 CP102D-XG03 | NE | MPC 4 SLOT 6 DANGER+ CH. 1
RL3
RL4
RL5
RL6
RL7
RL8
RL9 | MBM21 CP102C-XG01 | NE | MPC 4 SLOT 6 ALERT+ CH. 3
RL10 | MBM21 CP102D-XG03 | NE | MPC 4 SLOT 6 DANGER+ CH. 3
RL11
RL12
RL13
RL14
RL15
RL16
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Maximum BF: | [5 empty] | Maximum AF:
|  |  |  | MPC = 8 | [5 empty] | MPC = 4
|  |  |  | AMC = 16 | [5 empty] | AMC = 8

## Taper
Taper MAD12CY001M
Only change values in green table
| From | To
Angle (°) | 5 |  |  | Sin | 0.087156
Measuring range (mm) | -3 | 30.7 |  | Delta (mm) | 2.9371
Sensor (mV/µm) | 4 |  |  | Delta (mV) | 11748.5941
| mm | mV (Not inverted) | mV (Inverted) | Delta mV | mV / mm
Minimum | -3 | -15474.2971 | -3725.7029 | -1045.8689
Zero point | 0 | -14428.4281 | -4771.5719 |  | 348.623
Maximum | 30.7 | -3725.7029 | -15474.2971 | 10702.7252
Ok Level |  | -17600 | -1600
|  | -1600 | -17600
|  |  |  | 16000 | Available
|  |  |  | 11748.5941 | Used
2125.7029
Taper MAD13CY001M
Only change values in green table
| From | To
Angle (°) | 5 |  |  | Sin | 0.087156
Measuring range (mm) | -5 | 52 |  | Delta (mm) | 4.9679
Sensor (mV/µm) | 1.33 |  |  | Delta (mV) | 6607.2769
| mm | mV (Not inverted) | mV (Inverted) | Delta mV | mV / mm
Minimum | -5 | -12903.6384 | -6296.3616 | -579.5857
Zero point | 0 | -12324.0527 | -6875.9473 |  | 115.9171
Maximum | 52 | -6296.3616 | -12903.6384 | 6027.6912
Ok Level |  | -17600 | -1600
|  | -1600 | -17600
|  |  |  | 16000 | Available
|  |  |  | 6607.2769 | Used
4696.3616
MKD11CY022