## MPC MK2 Config.
MPC MK2 CONFIGURATION SLOT 3
| CMS license: | Yes/no
| IP address: | DHCP/xxx.xxx.xxx.xxx | from Front
| subnet mask: | DHCP/xxx.xxx.xxx.xxx
Channel | Input TAG No. | Front-end | Sensor OK Level | I/P SENS. | Sensor Power Supply | Sensor position | Processing | Filter settings | Measurement Type | Qualifier | FSD | 4-20mA or 10,0V DC | Danger - Level | Hysteresis | Delay | Latch | Alarm - Level | Hysteresis | Delay | Latch | Alarm + Level | Hysteresis | Delay | Latch | Danger + Level | Hysteresis | Delay | Latch | Trip Multiplier | DC O/P | Output TAG No.
CH. 1 | NSL_PROX_X | TQ 402 / IQS 900 | -1,6 ÷ -17,6 Volt | 8mV/µm |  | 45° | Shaft relative vibration | 1500 Hz | True Peak | True Peak | 0 - 355 µm | 4-20mA | [17 empty] | 1 | NSL_PROX_X
CH. 2 | MAD13CY041 | CA202/IPC707/GSI127 | 2000 ÷ 12000 mVDC | 77 mV/mm/sec |  | - | Bearing absolute vibration | 20-200Hz | True RMS | True RMS | 25 mm/sec | 4-20mA | [17 empty] | 2 | MAD13CY041
CH. 1 & 2
CH. 3 | MAD13CYA021 | CA202/IPC 707 | 7000 ÷ 17000 µA | 77µA/mm/s |  | - | Bearing absolute vibration | 10-500Hz | True RMS | True RMS | 20mm/s RMS | 4-20mA | [17 empty] | 3 | MAD13CYA021
CH. 4
CH. 3 & 4
AUX 1
AUX 2
MPC SIL MK2 CONFIGURATION SLOT 4
| CMS license: | Yes/no
| IP address: | DHCP/xxx.xxx.xxx.xxx | from Front
| subnet mask: | DHCP/xxx.xxx.xxx.xxx
Channel | Input TAG No. | Front-end | Sensor OK Level | I/P SENS. | Sensor Power Supply | Sensor position | Processing | Filter settings | Rectifier | Qualifier | FSD | 4-20mA or 10,0V DC | Danger - Level | Hysteresis | Delay | Latch | Alarm - Level | Hysteresis | Delay | Latch | Alarm + Level | Hysteresis | Delay | Latch | Danger + Level | Hysteresis | Delay | Latch | Trip Multiplier | DC O/P | Output TAG No.
CH. 1 | NSL_PROX_X | TQ 402 / IQS 900 | -1,6 ÷ -17,6 Volt | 8mV/µm | - 24 V | 0° | Shaft relative vibration | 1500 Hz | True Peak | True Peak | 0 - 355 µm | 0-10V | [17 empty] | 1
CH. 2 | NSL_PROX_Y | TQ 402 / IQS 900 | -1,6 ÷ -17,6 Volt | 8mV/µm | +24 V | 90° | Shaft relative vibration | 1500 Hz | True RMS | True RMS | 0 - 355 µm
CH. 1 & 2
CH. 3 | [8 empty] | True RMS | True RMS |  | 0-10V
CH. 4
CH. 3 & 4
AUX 1
AUX 2
MPC MK2 CONFIGURATION SLOT 5
| CMS license: | Yes/no
| IP address: | DHCP/xxx.xxx.xxx.xxx | from Front
| subnet mask: | DHCP/xxx.xxx.xxx.xxx
Channel | Input TAG No. | Front-end | Sensor OK Level | I/P SENS. | Sensor Power Supply | Sensor position | Processing | Filter settings | Rectifier | Qualifier | FSD | 4-20mA or 10,0V DC | Danger - Level | Hysteresis | Delay | Latch | Alarm - Level | Hysteresis | Delay | Latch | Alarm + Level | Hysteresis | Delay | Latch | Danger + Level | Hysteresis | Delay | Latch | Trip Multiplier | DC O/P | Output TAG No.
CH. 1 | NSL_PROX_X | TQ 402 / IQS 900 | -1,6 ÷ -17,6 Volt | 8mV/µm |  | 0° | Shaft relative vibration | 1500 Hz | True Peak | True Peak | 0 - 355 µm | 4-20mA | [17 empty] | 1
CH. 2
CH. 1 & 2
CH. 3 | [8 empty] | True RMS | True RMS |  | 4-20mA
CH. 4
CH. 3 & 4
AUX 1
AUX 2
CPUM CONFIGURATION SLOT 00
| IP address 1: | DHCP/xxx.xxx.xxx.xxx
| subnet mask 1: | DHCP/xxx.xxx.xxx.xxx
| IP address 2: | DHCP/xxx.xxx.xxx.xxx
| subnet mask 2: | DHCP/xxx.xxx.xxx.xxx

## IOC MK2 relays
Relay configuration IOC MK2 SLOT 3
REL. No. | Output TAG No. | NE/NDE | Latched | SIGNALs LOCATION
FAULT |  | NE | No
RL1 |  | NE/NDE | No
RL2 |  | NE/NDE | No
RL3 |  | NE/NDE | No
RL4 |  | NE/NDE | No
Relay configuration IOC SIL MK2 SLOT 4
REL. No. | Output TAG No. | NE/NDE | Latched | SIGNALs LOCATION
FAULT |  | NE | No
RL1 |  | NE/NDE | No
RL2 |  | NE/NDE | No
RL3 |  | NE/NDE | No
RL4 |  | NE/NDE | No
Relay configuration IOC MK2 SLOT 5
REL. No. | Output TAG No. | NE/NDE | Latched | SIGNALs LOCATION
FAULT |  | NE | No
RL1 |  | NE/NDE | No
RL2 |  | NE/NDE | No
RL3 |  | NE/NDE | No
RL4 |  | NE/NDE | No
Gx_TL_RPM

## RLC MK2 relays
Relay configuration RLC MK2 SLOT 1
REL. No. | Output TAG No. | NE/NDE | Latched | SIGNALs LOCATION
RL1 |  | NE | No
RL2 |  | NE | No
RL3 |  | NE | No
RL4 |  | NE | No
RL5
RL6
RL7
RL8
RL9
RL10
RL11
RL12
RL13
RL14
RL15
RL16
Relay configuration RLC SIL MK2 SLOT X
REL. No. | Output TAG No. | NE/NDE | Latched | SIGNALs LOCATION
RL1 |  | NE
RL2 |  | NE
RL3 |  | NE
RL4 |  | NE
RL5
RL6
RL7
RL8
RL9
RL10
RL11
RL12
RL13
RL14
RL15
RL16

## XMV MK2
XMV16 CONFIGURATION SLOT 13
Channel | Input TAG No. | Signal Type | Front-end | Signal Origin | Linked Through | I/P SENS. | DC Offset | Current / Voltage |  | Fix. Freq. / Order Track. |  | Speed Ref. | Bandwidth | FSD
T1
T2
T3 | MAD11CY045 | Speed | TQ902IQS900 | MPC Slot 3 Tacho 1 | Tacho Bus | [8 empty] | 5000RPM
T4
CH. 1 | MAD11CY041 | Dynamic | TQ902IQS900 | MPC Slot 3 Channel 1 | Raw Bus (0/32) | 4mV/µm |  |  | x |  | x | T3 | 25 Orders | 500µmpp
CH. 2
CH. 3
CH. 4
CH. 5
CH. 6
CH. 7
CH. 8
CH. 9
CH. 10
CH. 11
CH. 12
CH. 13
CH. 14
CH. 15
CH. 16

## XMC MK2
XMC16 CONFIGURATION SLOT 14
Channel | Input TAG No. | Signal Type | Front-end | Signal Origin | Linked Through | I/P SENS. | DC Offset | Current / Voltage |  | Fix. Freq. / Order Track. |  | Speed Ref. | Bandwidth | FSD
T1
T2
T3 | MAD11CY045 | Speed | TQ902IQS900 | MPC Slot 3 Tacho 1 | Tacho Bus | [8 empty] | 5000RPM
T4
CH. 1 | MAD11CY041 | Dynamic | TQ902IQS900 | MPC Slot 3 Channel 1 | Raw Bus (0/32) | 4mV/µm |  |  | x |  | x | T3 | 25 Orders | 500µmpp
CH. 2
CH. 3
CH. 4
CH. 5
CH. 6
CH. 7
CH. 8
CH. 9
CH. 10
CH. 11
CH. 12
CH. 13
CH. 14
CH. 15
CH. 16

## Taper
Taper MAD12CY001M
Only change values in green table
| From | To
Angle (°) | 5 |  |  | Sin | 0.087156
Measuring range (mm) | -3 | 30.7 |  | Delta (mm) | 2.9371
Sensor (mV/µm) | 4 |  |  | Delta (mV) | 11748.5941
| mm | mV (Not inverted) | mV (Inverted) | Delta mV | mV / mm
Minimum | -3 | -15474.2971 | -3725.7029 | -1045.8689
Zero point | 0 | -14428.4281 | -4771.5719 |  | 348.623
Maximum | 30.7 | -3725.7029 | -15474.2971 | 10702.7252
Ok Level |  | -17600 | -1600
|  | -1600 | -17600
|  |  |  | 16000 | Available
|  |  |  | 11748.5941 | Used
2125.7029
Taper MAD13CY001M
Only change values in green table
| From | To
Angle (°) | 5 |  |  | Sin | 0.087156
Measuring range (mm) | -5 | 52 |  | Delta (mm) | 4.9679
Sensor (mV/µm) | 1.33 |  |  | Delta (mV) | 6607.2769
| mm | mV (Not inverted) | mV (Inverted) | Delta mV | mV / mm
Minimum | -5 | -12903.6384 | -6296.3616 | -579.5857
Zero point | 0 | -12324.0527 | -6875.9473 |  | 115.9171
Maximum | 52 | -6296.3616 | -12903.6384 | 6027.6912
Ok Level |  | -17600 | -1600
|  | -1600 | -17600
|  |  |  | 16000 | Available
|  |  |  | 6607.2769 | Used
4696.3616
MKD11CY022