## RRS
VibroSmart Signal List
REVISION RECORD SHEET
Rev | Date | Description
1.09 | 2014-09-30 | Preliminary version
1.10 | 2014-10-22 | Preliminary version
1.11 | 2014-10-31 | First released version
1.12 | 2015-08-04 | Add Profibus/Profisafe sheet
1.13 | 2015-11-26 | Added rms-scaled peak-to-peak for process RS
1.14 | 2016-04-25 | Process Dual Smax added + Update sensors according to Meggitt sensor systems rev2.11
1.15 | 2016-05-31 | Minor changes
1.16 | 2016-07-15 | Minor changes - number of BF added
1.17 | 2016-08-12 | NB updated, add extraction type
1.18 | 2017-11-10 | SE120 OK level change from uV to µA
| Todo for | Dual processing (Smax, X-Ymax) still to be added in signal list
| next version | Scaled peak-peak qualifier to be added
Default Decay time / response time to be added depending on type of processing (TBC 400ms, 4700ms)
Check Decode Factor and Decode Offset calculation

## Procedure
1 | Preliminary
| a | Hide or delete the Profibus / Profifsafe sheet accordingly to your configuration.
| b | If there is no VSI hide or delete the bloc VSI and Modbus of the "VibroSmart Configuration" sheet
| c | If the VSI is a Profibus/Profisafe interface remove or hide the Modbus bloc of the "VibroSmart Configuration" sheet
1 | Duplicate the VSV300 data in function of the number of modules to configure.
| a | Select the lines 1 to 31
| b | Ctrl-C
| c | select the line 32
| d | Ctr-V
| e | Redo 1a to 1c for the number of VSV300
2 | Define the type of processing block per module
| a | Highlight in the row A and B the needed processing (e.g. AAB Accel #1, NB Accel #2, Tacho AUX).
Accel means there is no integration in the front end, Velocity equal to one integration
A maximum of 3 processing can be selected, and there can be only one of each #1 , #2 and AUX
| b | Hide or delete all the line not highlighted
| c | Redo 2a and 2b for each module
| d | Hide or delete the row A and B
| e | For process with two scalar data entity (e.g. mm/s and um), if the second data entity is not used, hide or remove the corresponding line.
3 | Complete the general information for each VSV300
| a | Label bottom: max 12 characteres, usually indicates the function of the module, or the part of the machinery being monitored (e.g. bearing name)
| b | Label top: completed by Meggitt SA with the SRN number of the base. Reference number used for the configuration and the monitoring.
| c | Complete the IP adress, Auto us avalaible only if a DHCP server is avalaible in the network
| d | MB: Each Measurement Block (MB) can have a maximum of 16 modules (VSV300 and VSI010).
| e | Node: inside a MB each module shall have a unique Node ID, if there is no special request keep 'X', it will be incremented at Meggitt SA production
| f | Redo 3a to 3e for each module
4 | Complete the data for each channel of each VSV300
| a | Select the channel for each line
| b | Input TAG and Analog Output TAG. By default both tags are the same, if necessary replace the formula of the Analog Output TAG to change it.
| c | Select the front-end from the list, the OK level and sensitivity (value and unit) are completed accordingly. If the OK level and sensitivity are not correct the formula shall be replaced by the value
| d | Complete the I/P sensitivity if needed
| e | Select the type of sensor power supply
| f | Leave the processing as it is
| g | Complete the filter settings. Respect the LP/HP ratio depending on the type of processing (no integration, single or dual integration)
| h | Change the physical quantity if needed, only cells not greyed out have multiple selections
| i | Select the qualifier (rectifier) type
| j | If there is an analog output (4-20mA DC or AC) indicate the corresponding FSD. The input dynamic will be selected by Meggitt SA depending on the sensor type, processing, alarm level, …etc
| k | Analog Out: two Analog Output can be configured in AC or DC (4..20mA) mode. Write a '1' and/or a '2' on the corresponding colomn/row.
| l | Complete the Danger-/Alarm-/Alarm+/Danger+ level, hysteresis and delay
| m | Complete the TripMultiplier value
| n | Redo 4a to 4m for each process and each module
Here is an exemple for one VSV300
5 | Relays
| a | The relay located on the VSV are local, so there is no need to indicated the module, only the channel and the function are mandatory.
| b | The relay located on the VSI can be driven by a combination of inputs comming from several module, we use the notation VSV300-1,1 where VSV300 is the Module name and 1,1 the Measuement Block followed by theNodeId
The same notation shall be used for the local inputs, use then VSI010-1,16
6 | VSI010 - Modbus
| a | For Modbus configuration,use the "Fieldbus bloc" of the sheet VibroSmart Config.
| b | Select Modbus TCP or Modbus RTU, and complete the IP address or the COM parameters (E1 means Even, 1 bit stop)
| 6.1 | Modbus TCP or Modbus RTU - default configuration
| a | If there is no specific mapping required, select the 4 existing lines, merge the lines and indicate "All registers as defined in the Hardware View"
| 6.2 | Modbus TCP or Modbus RTU - specific configuration
| a | Add as much line as needed, there should be one entry per register
| b | Complete each line with the corresponding information
7 | VIS010 - Profibus
Profibus provide 12 slots of 126 fileds. Each fields can be as well a bit or a byte.
Profisafe provide also 12 slots, bit the mapping of each slot is fixed, 4 bytes of 8 bits folowed by 4 Signed Short Integer of 2bytes.
| 7.1 | Slots creations
| a | Select the lines 3 to 10
| b | Ctrl-C
| c | select the line 11
| d | Ctr-V
| e | Redo7.1a to 7.1c for the number of Slot you need
| f | Rename the cells in column C to indicate the Slot number
| 7.2 | Registers creation
| a | Select the line 9
| b | Ctrl-C
| c | Right-Click on the number of the line 9, Insert Copier Cells
| d | Redo 7.2a to 7.2c for the number of Registers you need
| 7.2 | Registers completion
| a | For a bit the datatype shall be "Undefined Byte" and the column "bit#" shall be completed to indicate the position into the byte (0-based)
| b | Decode Factor and Decode Offset are calculated accordingly to FB and ENG values (to be validated)
8 | Complete the labeling
| a | Otherwise specified the "Label bottom" is dedicated for the SRN of the base (the one seen from VibroSight)
| b | Complete the "Label top" to indicates the function of the modules.

## VibroSmart Config.
|  | MB1, NodeX | VSV300 | Label top: | TBD |  |  | Label bottom (1): |  |  | #SER# |  |  |  | IP Adress: |  | Auto | [7 empty] | Meas. Block Nbr: |  | 1 |  | Node Id: | TBD
|  | Channel | Input TAG No. | Front-end | Sensor OK Level | Delay | I/P SENS. |  | SPS | HP | Processing (/ = Main Path) (F = Freq. dom.) |  | Filter settings / tacho ratio | Speed ref. | Physical quantity | Extraction type | Qualifier | Decay time | Full Scale Deflection | Analog Out. |  | Danger- |  | Alert- |  | Alert+ |  | Danger+ |  | Trip multiplier | Analog Output TAG
[20 empty] | DC | AC | Level | Hyst/Delay | Level | Hyst/Delay | Level | Hyst/Delay | Level | Hyst/Delay
AAB | Accel #1 | Ch.1 | TBD | TBD |  | 10s |  |  | -- Disable | 3Hz | / | AAB | 3 - 19000Hz |  | Acceleration |  | True RMS | 400ms | 250 m/s2 | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1 | TBD
[15 empty] | Velocity |  | Scaled Peak | 400ms
AAB | Accel #2 | Ch.2 | TBD | TBD |  | 10s |  |  | -- Disable | 3Hz | / | AAB | 3 - 19000Hz |  | Acceleration |  | Scaled Peak | 400ms | 250 m/s2 | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1 | TBD
[15 empty] | Velocity |  | Scaled Peak | 400ms
AAB | Velocity #1 | Ch.1 | TBD | TBD |  | 10s |  |  | -- Disable | 3Hz | / | AAB | 3 - 19000Hz |  | Velocity |  | Scaled Peak | 400ms | 100 mm/s | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1 | TBD
[15 empty] | Displacement |  | Scaled Peak | 400ms
AAB | Velocity #2 | Ch.2 | TBD | TBD |  | 10s |  |  | -- Disable | 3Hz | / | AAB | 3 - 19000Hz |  | Velocity |  | Scaled Peak | 400ms | 100 mm/s | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1 | TBD
[15 empty] | Displacement |  | Scaled Peak | 400ms
BBP | Pressure #1 | Ch.1 | TBD | TBD |  | 10s |  |  | -- Disable | 3Hz | / | BBP | 3 - 19000Hz |  | Dyn. Pressure |  | True RMS | 400ms | 250 m/s2 | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1 | TBD
[11 empty] | F |  | BStart=10Hz, BStop=10Khz
BBP | Pressure #1 | Ch.1 | TBD | TBD |  | 10s |  |  | -- Disable | 3Hz | / | BBP | 3 - 19000Hz |  | Dyn. Pressure |  | True RMS | 400ms | 250 m/s2 | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1 | TBD
[11 empty] | F |  | BStart=10Hz, BStop=10Khz
RS | Relative vib #1 | Ch.1 | TBD | TBD |  | 10s |  |  | -- Disable | 3Hz | / | RS | 1500Hz |  | Gap |  | Ini.gap = 9.6V | -
[15 empty] | Displacement |  | Scaled Peak | 4700ms | 250 um | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1 | TBD
RS | Relative vib #2 | Ch.2 | TBD | TBD |  | 10s |  |  | -- Disable | 3Hz | / | RS | 1500Hz |  | Gap |  | Ini.gap = 9.6V | -
[15 empty] | Displacement |  | Scaled Peak | 4700ms | 250 um | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1 | TBD
Smax | Dual | Dual | TBD | [7 empty] | X-Y max discriminator (ISO 7919-1 Method B) |  |  |  | Smax |  | True Peak | 400 ms |  | 1 | [10 empty] | TBD
NB | Accel #1 | Ch.1 | TBD | TBD |  | 10s |  |  | -- Disable | 3Hz | / | NB | 6.25 [nX] | AUX | Acceleration | BandPeak | Band Peak | - | 250 m/s2 | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1 | TBD
[13 empty] | MinSpeed=0.0256Hz,MaxSpeed=624Hz |  | Band start= nX, Band stop= nX |  |  | -
NB | Accel #2 | Ch.2 | TBD | TBD |  | 10s |  |  | -- Disable | 3Hz | / | NB | 6.25 [nX] | AUX | Acceleration | BandPeak | Band Peak | - | 250 m/s2 | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1 | TBD
[13 empty] | MinSpeed=0.0256Hz,MaxSpeed=624Hz |  | Band start= nX, Band stop= nX |  |  | -
NB | Velocity #1 | Ch.1 | TBD | TBD |  | 10s |  |  | -- Disable | 3Hz | / | NB | 3 - 19000Hz | AUX | Velocity |  | Scaled Peak | - | 100 mm/s | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1 | TBD
[15 empty] | Displacement |  | Scaled Peak | -
NB | Velocity #2 | Ch.2 | TBD | TBD |  | 10s |  |  | -- Disable | 3Hz | / | NB | 3 - 19000Hz | AUX | Velocity |  | Scaled Peak | - | 100 mm/s | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1 | TBD
[15 empty] | Displacement |  | Scaled Peak | -
Position | Channel #1 | Ch.1 | TBD | TBD |  | 10s |  |  | -- Disable | -- | / | Position |  | AUX | Position |  | Ini.gap = 9.6V | - | +/-1mm | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1 | TBD
Position | Channel #2 | Ch.2 | TBD | TBD |  | 10s |  |  | -- Disable | -- | / | Position |  | AUX | Position |  | Ini.gap = 9.6V | - | +/-1mm | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1 | TBD
Position | AUX | AUX | TBD | TBD |  | 10s |  |  | -- Disable | -- | / | Position |  | AUX | Position |  | Ini.gap = 9.6V | - | +/-1mm | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1 | TBD
Tacho | AUX | AUX | TBD | TBD |  | 10s |  |  | -- Disable | -- | / | Tacho | 1-1-1 |  | Speed |  | Ini.gap = 9.6V | - | 3000rpm | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1 | TBD
|  | MB1, NodeX | VSI010 | Label top: | TBD |  |  | Label bottom (1): |  |  | #SER# |  |  |  | IP Adress: |  | Auto | [7 empty] | Meas. Block Nbr: |  | 1 |  | Node Id: | TBD
Relays
|  |  | VSV300-1,1 | Relay | TAG |  |  |  | NE/NDE |  |  | Latched | Function | [15 empty] | #BF | #AF
|  |  |  | RL1 | TBD |  |  |  | NE |  |  | Yes | (Ch1 RS Vibration - D+) AND (Ch1 OK) | [15 empty] | 1 | 0
|  |  |  | RL2 | TBD |  |  |  | NE |  |  | Yes | (Ch1 NOT OK) OR (Ch2 NOT OK) OR (Aux NOT OK) | [15 empty] | 1 | 0
|  |  | VSV300-1,2 | Relay | TAG |  |  |  | NE/NDE |  |  | Latched | Function
|  |  |  | RL1 | TBD |  |  |  | NE |  |  | Yes | (Ch1 AAB Velocity - D+) AND (Ch1 OK) | [15 empty] | 1 | 0
|  |  |  | RL2 | TBD |  |  |  | NE |  |  | Yes | (Ch1 NOT OK) OR (Ch2 NOT OK) OR (Aux NOT OK) | [15 empty] | 1 | 0
|  |  | VSI010-1,16 | Relay | TAG |  |  |  | NE/NDE |  |  | Latched | Function
|  |  |  | RL1 | TBD |  |  |  | NE |  |  | No | ((VSV300-1,1 - Ch1 RS Vibration - D+) AND (VSV300-1,1 - Ch1 OK)) OR ((VSV300-1,2 - Ch1 AAB Velocity - D+) AND (VSV300-1,2 - Ch1 OK)) | [15 empty] | 2 | 1
|  |  |  | RL2 | TBD |  |  |  | NE |  |  | No | ((VSV300-1,1 - Ch1 NOT OK) OR (VSV300-1,1 - Ch2 NOT OK) OR (VSV300-1,1 - Aux NOT OK) OR (VSV300-1,2 - Ch1 NOT OK) OR (VSV300-1,2 - Ch2 NOT OK) OR (VSV300-1,2 - Aux NOT OK) | [15 empty] | 1 | 0
|  |  | VSV300/301 : Number of BF=4, AF=2 |  | A Basic Function (BF) is requested for each product term with unique operator (AND, OR or VOTE). Each term can be inverted or not.
|  |  | VSV010: Number of BF=8, AF=4 |  | An AdvanceFunction (AF) is requested for each combination of product term, operator can be AND, OR and VOTE. Each term can be inverted or not.
Modbus
[5 empty] | Type: | Modbus TCP | [8 empty] | Modbus IP Adress: |  |  | 127.0.0.1 |  |  |  | COM |  | COM1, 9600, E1
|  |  | VSI010-1,16 | Address (0 based) | Unit | Qualifier |  |  | Data type |  |  |  | ByteOrder | Measurement |  |  | Measurement
|  |  |  | 0x0000001 | N/A | N/A |  |  | Byte (1byte) |  |  |  | N/A | VSV300-1,1 > Ch1 > Danger+
|  |  |  | 0x0000002 | N/A | N/A |  |  | Byte (1byte) |  |  |  | N/A | VSV300-1,1 > Ch1 > Alarm+
|  |  |  | 0x0000003 | True RMS | m/s2 |  |  | Double (8bytes) |  |  |  | Big endian | VSV300-1,1> Ch1 > Amplitude
|  |  |  | 0x0000004 | True RMS | g |  |  | Double (8bytes) |  |  |  | Big endian | VSV300-1,1 > Ch1 > Amplitude
(1) Label bottom is by default reserved for the serial number of the modules. For any other pupose please contact Meggitt SA.
|  |  | Band Peak | Band Energy | Harmonics | Not 1X | Sub-Harmonics
|  |  | Band Peak | RMS | RMS | RMS | RMS
|  |  |  | Average | Average | Average | Average
|  |  |  | Peak | Peak | Peak | Peak
|  |  |  | Peak-peak | Peak-peak | Peak-peak | Peak-peak
Note on AE2: Equivalent to module Nbr
Note on H4: Not OK to OK [0.1sec to 60 sec]
Note on K4: Sensor power supply
Note on L4: Analog High Pass filter: - Disabled (for NB and Pos processings) - 0.1 Hz - 1 Hz - 3 Hz (default)
Note on O4: LP/HP filter ratio: <=1000 if a single integration is used. <=100 if a double integration is used. If no integration is used: No LP/HP restriction if digital HP filter cut-off freq >=3Hz. <=400 if digital HP filter cut-off freq <3Hz.
Note on P4: speed ref: can come from the local module or from a remote module (of the same Measurement Block)
Note on S4: May be better known as "Rectifier"
Note on U4: Output FSD. Input FSD is selected depending on the sensor type.
Note on U6: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s
Note on U7: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s Displacement unit: µm, mils Distance unit: m, mm, cm, µm, in, mils Position unit: m, cm, mm. µm Gap unit: mm, in. mils Airgap unit: mm, cm
Note on U8: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s
Note on U9: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s Displacement unit: µm, mils Distance unit: m, mm, cm, µm, in, mils Position unit: m, cm, mm. µm Gap unit: mm, in. mils Airgap unit: mm, cm
Note on U10: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s
Note on U11: Displacement unit: µm, mils Distance unit: m, mm, cm, µm, in, mils Position unit: m, cm, mm. µm Gap unit: mm, in. mils Airgap unit: mm, cm
Note on U12: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s
Note on U13: Displacement unit: µm, mils Distance unit: m, mm, cm, µm, in, mils Position unit: m, cm, mm. µm Gap unit: mm, in. mils Airgap unit: mm, cm
Note on U14: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s
Note on Q15: Only for frequency domain
Note on U15: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s Displacement unit: µm, mils Distance unit: m, mm, cm, µm, in, mils Position unit: m, cm, mm. µm Gap unit: mm, in. mils Airgap unit: mm, cm
Note on U16: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s
Note on Q17: Only for frequency domain
Note on U17: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s Displacement unit: µm, mils Distance unit: m, mm, cm, µm, in, mils Position unit: m, cm, mm. µm Gap unit: mm, in. mils Airgap unit: mm, cm
Note on U19: Unit: mm, in
Note on U21: Unit: mm, in
Note on U24: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s Displacement unit: µm, mils Distance unit: m, mm, cm, µm, in, mils Position unit: m, cm, mm. µm Gap unit: mm, in. mils Airgap unit: mm, cm
Note on U26: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s Displacement unit: µm, mils Distance unit: m, mm, cm, µm, in, mils Position unit: m, cm, mm. µm Gap unit: mm, in. mils Airgap unit: mm, cm
Note on U27: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s
Note on U28: Displacement unit: µm, mils Distance unit: m, mm, cm, µm, in, mils Position unit: m, cm, mm. µm Gap unit: mm, in. mils Airgap unit: mm, cm
Note on U29: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s
Note on U30: Displacement unit: µm, mils Distance unit: m, mm, cm, µm, in, mils Position unit: m, cm, mm. µm Gap unit: mm, in. mils Airgap unit: mm, cm
Note on U31: Unit: mm, in
Note on U32: Unit: mm, in
Note on U33: Unit: mm, in
Note on U34: Unit: rpm,Hz

## VSV300 ref (hidden)
µ
Dynamic input - Processing bloc
Channel | Input TAG No. | Front-end | Sensor OK Level | Delay | I/P SENS. | PS | HP | Processing (/ = Main Path) |  | Filter settings | Speed ref. | Extr. type | Physical quantity | Rectifier (Qualifier) | FSD | Analog Out. |  | Danger- |  | Alert- |  | Alert+ |  | Danger+ |  | Triple multiplier | Analog Output TAG
[16 empty] | DC | AC | Level | Hyst./Del. | Level | Hyst./Del. | Level | Hyst./Del. | Level | Hyst./Del.
Asynchronous Absolute Bearing Vibration Processing
TBD | TBD | CAxxx + IPC + GSI | 2000mV .. 12000mV | 0s | 0mV/g | -- Disable | 3Hz | / | AAB | 3 - 19000Hz |  |  | Acceleration | Scaled Peak | 250 m/s2 | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1.5 | TBD
[13 empty] | Velocity | Scaled Peak | 100 mm/s
TBD | TBD | CAxxx + IPC (Integ.) + GSI | 2000mV .. 12000mV | 0s | 0mV/mm/s | -- Disable | 3Hz | / | AAB | 3 - 19000Hz |  |  | Velocity | Scaled Peak | 100 mm/s | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1.5 | TBD
[13 empty] | Displacement | Scaled Peak | 200 µm
Shaft Relative Vibration Processing
TBD | TBD | TQ4x2 + IQS[I] (2mm) | -1600mV .. -17600mV | 0s |  | -24 V | 3Hz | / | RS | 3 - 19000Hz |  |  | Position | Ini.gap = 9.6V
[13 empty] | Acceleration | Scaled Peak | 10g | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1.5 | TBD
Narrow Band Vibration Processing | [11 empty] | Band Peak: 10 - 1000Hz; Band Energy: 10 - 1000Hz; Harmonics: 2x, Not 1x, Sub-Harmonic: 1/2x
TBD | TBD | CE31X + GSI127 | 500mV - 3000mV | 0s | 250mV/g | -- Disable |  | / | NB - 25[nX] | 0.0167 - 600Hz | Aux | Band Energy: 10 - 1000Hz | Acceleration | Scaled Peak | 250 m/s2 | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1.5 | TBD
[13 empty] | Velocity | Scaled Peak | 100 mm/s
[13 empty] | Displacement | Scaled Peak | 200 µm
Position Processing
TBD | TBD | TQ412 + IQS450 + GSI127 | -3500mV - -100mV | 0s | 8mV/µm | -24 V | 0.1 Hz | / | Position | Inverted |  |  | Position | Ini.gap = 9.6V | [7 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1.5 | TBD
Broad Band Pulsation Processing
TBD | TBD | CP103 + GSI127 | 500mV - 3000mV | 0s | 250mV/bar | -- Disable | 3Hz | / | BBP | 3 - 19000Hz |  |  | Pressure | Scaled Peak | 1 bara | 1 | [5 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1.5 | TBD
Dynamic input - Dual Processing bloc
Channel | Input TAG No. | Front-end | Sensor OK Level | HP | I/P SENS. | PS | HP | Processing (/ = Main Path) |  | Filter settings | Speed ref. | Extr. type | Physical quantity | Rectifier (Qualifier) | FSD | Analog Out. |  | Danger- |  | Alert- |  | Alert+ |  | Danger+ |  | Triple multiplier | Analog Output TAG
[16 empty] | DC | AC | Level | Hyst./Del. | Level | Hyst./Del. | Level | Hyst./Del. | Level | Hyst./Del.
Smax
TBD
Orbit
TBD
Aux input - Processing bloc
Channel | Input TAG No. | Front-end | Sensor OK Level | HP | I/P SENS. | PS | HP | Processing (/ = Main Path) |  | Filter settings | Speed ref. | Extr. type | Physical quantity | Rectifier (Qualifier) | FSD | Analog Out. |  | Danger- |  | Alert- |  | Alert+ |  | Danger+ |  | Triple multiplier | Analog Output TAG
[16 empty] | DC | AC | Level | Hyst./Del. | Level | Hyst./Del. | Level | Hyst./Del. | Level | Hyst./Del.
Tacho Processing
AUX | TBD | TQ412 + IQS450 + GSI127 | -3500mV - -100mV | 0s | 8mV/µm | -24 V | 0.1 Hz | / | Tacho | 1 * 1 / 1 | [11 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1.5 | TBD
Position Processing
AUX | TBD | TQ412 + IQS450 + GSI127 | -3500mV - -100mV | 0s | 8mV/µm | -24 V | 0.1 Hz | / |  | Inverted |  |  | Position | Ini.gap = 9.6V | [7 empty] | 102 | 0 / 3s | 178 | 0 / 1s | 1.5 | TBD
Note on R3: Unit are in FSD unit Delay is in second
Note on F8: Not OK to OK
Note on L8: Ratio: 1000 if only a single integration is used (velocity) 100 if a dual integration is used (displacement)
Note on Q9: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s Displacement unit: µm, mils Distance unit: m, mm, cm, µm, in, mils Position unit: m, cm, mm. µm Gap unit: mm, in. mils Airgap unit: mm, cm
Note on F11: Not OK to OK
Note on L11: Ratio: 1000 if only a single integration is used (velocity) 100 if a dual integration is used (displacement)
Note on Q11: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s
Note on Q12: Displacement unit: µm, mils Distance unit: m, mm, cm, µm, in, mils Position unit: m, cm, mm. µm Gap unit: mm, in. mils Airgap unit: mm, cm
Note on F16: Not OK to OK
Note on L16: Ratio: 1000 if only a single integration is used (velocity) 100 if a dual integration is used (displacement)
Note on F21: Not OK to OK
Note on L21: Limit: TBD
Note on Q22: Velocity unit: m/s, mm/s, in/s Speed unit: m/s, mm/s
Note on Q23: Displacement unit: µm, mils Distance unit: m, mm, cm, µm, in, mils Position unit: m, cm, mm. µm Gap unit: mm, in. mils Airgap unit: mm, cm
Note on F27: Not OK to OK
Note on F33: Not OK to OK
Note on L33: Ratio: 1000 if only a single integration is used (velocity) 100 if a dual integration is used (displacement)
Note on R38: Unit are in FSD unit Delay is in second
Note on R50: Unit are in FSD unit Delay is in second
Note on F55: Not OK to OK
Note on L55: Ratio: 1 * (1 / 1) Number of Teeth * (
Note on F59: Not OK to OK

## Profibus
Profibus
| Slot 0 | Address (decimal, 0-based) | DataType | bit# | #byte | ByteOrder | Unit | Qualifier | Min FB value | Min ENG value | Max FB value | Max ENG value | Decod Factor | Decod Offset | Process Output
|  | 0 | Unsigned Byte (1 byte) | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 ULF
|  | 0 | Unsigned Byte (1 byte) | 2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 LF
|  | 1 | Short Integer (2bytes) | N/A | 4 | Little endian | mbar | True RMS | -16384 | 0 | 16383 | 200 | 0.0061037 | 0 | MBM10CP010 Burner 1 HF 1200-7000 Hz Pulsation
|  | 7 | Short Integer (2bytes) | N/A | 2 | N/A | mbar | Scaled Peak | -16384 | 0 | 16383 | 200 | 0.0061037 | 0 | MBM10CP010 Burner 1 LF 20-300 Hz Pulsation
|  | 9 | Double (8bytes) | N/A | 4 | Little endian | mbar | True Peak | N/A | N/A | N/A | N/A | N/A | N/A | MBM10CP010 Burner 1 LF 300-2000 Hz Pulsation

## Profisafe
Profisafe
| Slot0 | Address (decimal, 1-based) | DataType | bit# | #byte | ByteOrder | Unit | Qualifier | Min FB value | Min ENG value | Max FB value | Max ENG value | Decod Factor | Decod Offset | Process Output
|  | 0 | Bit | 0 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 ULF
|  | 0 | Bit | 1 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 LF
|  | 0 | Bit | 2 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 MF
|  | 0 | Bit | 3 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 HF
|  | 0 | Bit | 4 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP010 Burner 2 ULF
|  | 0 | Bit | 5 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP010 Burner 2 LF
|  | 0 | Bit | 6 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP010 Burner 2 MF
|  | 0 | Bit | 7 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP010 Burner 2 HF
|  | 1 | Bit | 0 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 ULF
|  | 1 | Bit | 1 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 LF
|  | 1 | Bit | 2 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 MF
|  | 1 | Bit | 3 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 HF
|  | 1 | Bit | 4 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP010 Burner 2 ULF
|  | 1 | Bit | 5 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP010 Burner 2 LF
|  | 1 | Bit | 6 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP010 Burner 2 MF
|  | 1 | Bit | 7 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP010 Burner 2 HF
|  | 2 | Bit | 0 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 ULF
|  | 2 | Bit | 1 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 LF
|  | 2 | Bit | 2 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 MF
|  | 2 | Bit | 3 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 HF
|  | 2 | Bit | 4 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP010 Burner 2 ULF
|  | 2 | Bit | 5 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP010 Burner 2 LF
|  | 2 | Bit | 6 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP010 Burner 2 MF
|  | 2 | Bit | 7 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP010 Burner 2 HF
|  | 3 | Bit | 0 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 ULF
|  | 3 | Bit | 1 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 LF
|  | 3 | Bit | 2 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 MF
|  | 3 | Bit | 3 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP005 Burner 1 HF
|  | 3 | Bit | 4 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP010 Burner 2 ULF
|  | 3 | Bit | 5 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP010 Burner 2 LF
|  | 3 | Bit | 6 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP010 Burner 2 MF
|  | 3 | Bit | 7 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Data quality bit MBM10CP010 Burner 2 HF
|  | 4 | Signed short Int |  | 2 | N/A | mbar | True RMS | -16384 | 0 | 16383 | 500 | 0.015259 | 0 | MBM10CP005 Burner 1 ULF 20-60 Hz Pulsation
|  | 6 | Signed short Int |  | 2 | N/A | mbar | True RMS | -16384 | 0 | 16383 | 500 | 0.015259 | 0 | MBM10CP005 Burner 1 LF 60-300 Hz Pulsation
|  | 8 | Signed short Int |  | 2 | N/A | mbar | True RMS | -16384 | 0 | 16383 | 500 | 0.015259 | 0 | MBM10CP005 Burner 1 MF 300-1200 Hz Pulsation
|  | 10 | Signed short Int |  | 2 | N/A | mbar | True RMS | -16384 | 0 | 16383 | 500 | 0.015259 | 0 | MBM10CP005 Burner 1 HF 1200-7000 Hz Pulsation