## Slide 1: Overview of IEC 61850 – GOOSE Vibrosmart
  presented by Samuel Delabays
  Technical Support
    March 2022

## Slide 2: Smart Grid
Transformation of the industry  digital transformation of the infrastructure
generation
market
transmission
distribution
consumer
few, large power plants
centralized, mostly national
based on power lines and pipelines
top to bottom
passive, only paying
many, small power producers
decentralized, ignoring boundaries
including small-scale transmission
and regional supply compensation
both directions
active, participating in the system

## Slide 3: Main issues with modern power grid
Fast growth and unpredictability (wind, solar, etc)
Cybersecurity risks
Aging infrastructure
No common standards

## Slide 4: IEC 61850
Focused on improving the automation of electrical substations*
Interoperability: avoidance of proprietary protocols and easier integration of equipment from different manufacturers.
Economy: technologies that can reduce the amount of wiring and engineering time.
Maintainability: improvements in the commissioning and maintenance tasks.
*WHAT IS AN ELECTRICAL SUBSTATION?
Substations transform voltage from high to low (or vice-versa) and perform several other critical functions. Before power reaches the consumer from the generating station, it is likely to flow through several substations at different voltage levels.

## Slide 5: GOOSE
Generic Object-Oriented Substation Event
GOOSE is a communication model defined in IEC 61850
It features ultra-high messaging speed and improved reliability needed for sequence-of-event reconstruction where events may be separated by milliseconds.
IEC 61850 is a family of standards; GOOSE is only a small part of the standard’s content
  Part 7-1
  Part 8-1
Generic Object-Oriented Substation Event

## Slide 6: GOOSE - Generic Object-Oriented Substation Event
Other competing protocols:
DNP3
EIP
Profibus
Profinet
Modbus
UCA2
IEC 608070-5-X
Why are we implementing it?
Owners of both Power Generation and power transmission/distribution show clear interest in IEC-61850 approach for remote control and data collection from grids and power plants.
GOOSE is often preferred over other protocols for substation automation and control because of its advanced features and capabilities, robustness, and reliability in harsh industrial environments, and ability to support real-time communication and advanced diagnostic information.
Hydro-Québec VibroSmart pilot project:
    Joint work on integration of IEC 61850 VibroSmart solution into existing HQ
    remote monitoring and control system for the whole fleet of HQ facilities
    GOOSE protocol implementation
    Limited support of SCL configuration features

## Slide 7: What is our IED?
Intelligent Electronic Device
The VSI010 is a IED
In the context of GOOSE communication protocol, an IED (Intelligent Electronic Device) is a device that is used to monitor and control various electrical and automation systems. An IED typically contains digital inputs and outputs, and communication interfaces, and is capable of processing and exchanging information with other devices and systems in real-time.

## Slide 8: VibroSmart implementation – Block diagram Concept implemented at Hydro Québec
VSI010
IEC61850
GOOSE protocol
NETWORK
SMART RELAY
VSV30x
VSV30x
VSV30x
VSV30x
IEC61850
GOOSE protocol
GOOSE Publisher
GOOSE Subscriber
IEC 61850 – GOOSE
16 February 2023
8

## Slide 9: VibroSmart implementation – Configurator – VSI GOOSE interface
IEC 61850 – GOOSE
16 February 2023
9

## Slide 10: PTP synchronization Vibrosmart
GSM – Abu Dhabi
  presented by Samuel Delabays,
  Technical Support
    March 2022

## Slide 11: The Precision Time Protocol (PTP) is used to synchronize clocks throughout a network. Allow accurate event correlation
Both NTP (Network Time Protocol) and PTP (Precision Time Protocol) use network to serve time to other devices and achieve time synchronization.
Firmware release prior 642-001-000-019 only provided NTP synchronization between the VibroSmart devices and other systems. The PTP synchronisation was only performed between VSV30x modules. With FW -020 and newer, it is now possible to sync the VSV30X modules to either a NTP or a PTP server.
With NTP, the VSV30x were able to achieve time synchronisation between 2 – 10ms and in some cases up to 50ms.
With PTP, the VSV30x can synchronise waveform measurement to sub-millisecond in order to correlate events from VibroSmart system with other systems such as circuit breakers or electrical events and allow accurate analysis (chain of events etc). Also the PTP synchronisation between module has been improved and the display sync has been redesigned in VibroSight vision enabling the “Elapsed Time” view for the waveform plot.

## Slide 12: VibroSmart® PTP synchronization - Concept
  Addition of PTP protocol with VSV30x. Tests showed that millisecond sync is achieved for waveform measurements between modules.
VSV #2
VSV #1
PTP server
Δ ≤1ms
3rd party devices
GPS SAT
VSN010
PTP Layer 2 (or layer 3)
PTCP protocol definition within the Profinet context
The VSN010 runs the PTP deamon and acts as a bridge between PTP and PTCP
DIGITAL PLANT - PTP
12
16 February 2023

## Slide 13: PTP – Test results
13
16 February 2023
DIGITAL PLANT - PTP